## Slide 1: Distribution Operation Centers – Integrating Technology & Data Analytics
February 19, 2019
Speaker(s): | Mathew Tovar, PE Travis Kennedy, PE

## Slide 2: Distribution Operation Centers
Central hub for distribution outages
  Every distribution power outage comes through the DOCs
  An operator dispatches a resource to the ticket
  An operator will direct switching & perform remote operations
East & West DOC
  Oncor has 2 DOCs

## Slide 3: Distribution Operation Centers
Agenda:
  DOC Operations of Today
  Data Analytics at the DOCs

## Slide 4: Distribution Operation Centers – Historically
Outages reported via phone calls
Paper maps & one lines
Paper event tickets
Experience & gut feel to determine load
Priority switching to find faults

## Slide 5: Distribution Operation Centers – Presently
Outages reported from AMS, SCADA, Text Messages, Calls
OMS (Outage Management System) maps
  Tracking of trucks & resources
  Electronic tickets
  Real time SCADA load readings
  Calculated load readings on EVERY device in OMS
  Fault Maps from CYME & Fault Locating (FLOC)
  Data Analytics
  Predicting weather damage, overloads, equipment failures
  Monitoring power quality, construction projects, and creating contingency plans
  Creating helpful tools for the operators & districts

## Slide 6: Distribution Operation Centers – AMS & SCADA
AMS DATA
  Approx. 40TB daily (3.6 Million Meters)
  15 minute intervals
  Transmitted to OMS
  Stored in Oncor’s Enterprise Data Warehouse (EDW)
SCADA DATA
  Station RTUs
  Approx. 5-10 second intervals
  Transmitted to TMS & OMS
  Stored in Oncor’s Enterprise Data Warehouse (EDW)

## Slide 7: Distribution Operation Centers – AMS & SCADA
Distributed
Automation
DMS
Spectrum
Advanced Meter
System
DIS
CC&B
Smart Grid
Reports
Web
TXT
Kubra
(iFactor)
Remote
Terminal
Units
TMS
Workstations
TMS
Spectrum
DMS
Workstations
Mobile
Computers
OMS
In-Service
I/Dispatch
Net/Dispatch
Mobile TC
OTS
Workstations
OTS
Spectrum

## Slide 8: Distribution Operation Centers – OMS

## Slide 9: Distribution Operation Centers – OMS
Features
  AMS integration
  Dynamic ETOR calculations
  Event tickets & dispatching
  Fault Locating

## Slide 10: Distribution Operation Centers – ETOR
ETOR = Estimated Time of Restoration
Time to dispatch
First responder queue, travel, and repair time
Crew travel and repair time
Resource availability
Weather conditions
Location
Cause
Event workload
Real-Time Data
Historical Data

## Slide 11: Distribution Operation Centers – ETOR Public Communication
  Stormcenter.Oncor.com
  Text Oncor
  Interactive Voice Recognition (IVR)
  Call Center (CTA)

## Slide 12: Distribution Operation Centers – ETOR
ETOR = Estimated Time of Restoration

## Slide 13: Distribution Operation Centers – Customer Photos
WUPIT = Wire down, Unit on Site Process Improvement Tool
New process for identifying and acting on potentially hazardous situations to the public.
  Improves on existing communication between Operator and Customer
  Enhances safety with provided photos submitted from customers or first responders associated with emergency ticket
  Enhanced training for call center and affected Oncor employees and contractors
  Improves distribution of Damage Evaluation resources

## Slide 14: Distribution Operation Centers – Customer Photos
14,843
Number of photos submitted by customers
2,872
Number of events with photos
4
Average number of photos per event
6403
Number of text messages sent
The ability to submit photos helps a customer feel empowered. We hear them, we see them, we respond to them.
*Values from Feb 2018 – Jan 2019
Notes: Average 3% of events have photos (goes up in storms)
Barrier: Dealing with FD dispatchers and they don’t want to give out fireman phone numbers

## Slide 15: Distribution Operation Centers – Customer Photos
Notes: Talking points this slide:
    Remote disconnect for safety - operator could clearly see primary wire (25kv) was down, but was it energized?
        Checked for outages in immediate area (none reported)
        Located closest available field resource (at least one hour away)
        Meter ping verification (meters indicated energized)
        Open closest up line SCADA device (hazard removed)

## Slide 16: Distribution Operation Centers – Customer Photos
Notes: Talking points this slide:
Wire down report pole to house
  no sparking/arcing
  high traffic area
  across vehicle
Photo clearly shows:
  meter base pulled off wall
    Customer repairs required
  Low wire across parking areas
  Wire laying on top of customer’s car
  Transformer fuse still closed
Is the service still energized?
  Verified de-energized through meter ping
  Right resource (cut and roll truck) was sent to location (eliminating multiple trips by different work groups) and customer was contacted and left with instructions

## Slide 17: Distribution Operation Centers – Storms
Intelligent OMS
  Self aggregating outages
  Feeder lock out portal
Smart Grid Reports
  One place to find all reports
  Quickly assess any issues

## Slide 18: Distribution Operation Centers – Data Analytics
One of the Oncor’s Guiding Principles
“Use data and science to manage our functions, operations, and deliver to our customers and stakeholders”
IBM Software Package:
  Spark, R, SPSS, SAS, .Net, Scala
  Machine Learning Tools
Use Cases:
  Load Forecasting
  SAIDI from AMS
  Weather Damage Prediction
  Unauthorized DG Detection
  OMS Playback
  Cold Load PU Prediction
  Aerial Images Object Recognition

## Slide 19: Data Analytics – Load Forecasting
Summer & Winter Reports:
  Feeder Overload Predictions
  Substation Transformer Overload Predictions
Tools:
  Load predictions in OMS
  Estimated Load Forecast (ELF) Tool for feeders
  Estimated Load Forecast (ELF) Tool for substation transformers

## Slide 20: Data Analytics – Load Forecasting

## Slide 21: Data Analytics – SAIDI from AMS
SAIDI = SYSTEM AVERAGE INTERRUPTION DURATION INDEX
  Tracks interruptions greater than 5 minutes
  Average Outage Duration For Every Customer
Traditionally:
  Driven by the Connectivity Model through OMS
  OMS: OUTAGE MANAGEMENT SYSTEM
    Tracks customer, meter, and device reported outages
    Can infer other customers affected based on the connectivity model
With AMS:
  AMS/AMI (ADVANCED METERING SYSTEM)
    15 minute interval data
      Average Voltage
      kWh +/-
        Separate channels for consumed and generated energy
      Status flags
        Power Fails and Clock status
        How much data in the interval
    Unsolicited Power Status Events
      Last Gasp (Lost Power)
      Restoration (Restored Power)

## Slide 22: Data Analytics – SAIDI: AMS vs OMSR

## Slide 23: Data Analytics – Weather Damage Prediction
Data:
  Historical Outage Data
    Based on creation time, cause code, device, customer count, and geographic location
  Historical Weather Data
    Weather 4 hourly max, avg. and min based on customer density
    Temp, wind chill, wind, wind gust, rain, and snow
Modeling Techniques
  SPSS
Benefits:
  Staging of Resources
  Shorter Restoration Times

## Slide 24: Data Analytics – Unauthorized DG Detection
Identify all the meters with negative kWH readings across the system in last week
Include only the meters with increasing - kwH readings
Exclude all the customers who are authorized (agreement complete) and the customers who initiated the process
Identify any oil companies and exclude from the list
Extract only the residential meters based on meter type
Filter for customers whose -kWH is greater than 200kWH
Goal is to detect tampering and detection of DG is an ancillary benefit of the effort
Manual process with the use of spreadsheets for the data analysis

## Slide 25: Data Analytics – OMS Playback
Digital Data Twin:
  A replication of all data in OMS
  Replay events & perform RCAs

## Slide 26: Data Analytics – Cold Load Pickup Prediction
Cold Load Pick Up:
  When a typical load has been without supply for a period of time (hours) it loses its diversity. When power is restored the load is higher than usual.
Data & Relationship:
  Ambient Temperature
  Time of day
  Season – Summer or Winter
  Outage Duration – 30 minutes vs 4 hours
  Type of Load – Residential, Non-Residential and Commercial/Industrial

## Slide 27: Data Analytics – Aerial Imagery Object Recognition
Proposed Use Cases:
  Post Storm Damage Assessment
  Seasonal Wildfire Risk Assessment
  Seasonal Structure Erosion Assessment
  Post Storm Flood Detection
  Annual Easement Intrusion Detection
Software:
  Microsoft Azure Custom Vision
  Working near the Cloud
Image Sources:
  University of Texas
  SkySat
  Oncor Transmission
  Google Earth

## Slide 28: Data Analytics – Aerial Imagery Machine Learning

## Slide 29: Data Analytics – Aerial Imagery Object Recognition

## Slide 30: Data Analytics – Aerial Imagery Object Recognition
Image Type & Quality
  Satellite (1 meter per pixel)
    Refresh Rate: 2x a day - Once a quarter
  Fixed Wing & Drone
    Altitude & Angle
    Turn Around: 3-5 days

## Slide 31: Data Analytics – Aerial Imagery Object Recognition
Azure Custom Vision - Cloud Based Program
  Oncor ARB (Architect Review Board) has approved
  Images from source to Custom Vision
  Download trained model via Docker container to run on prem.

## Slide 32: Questions or Comments?