## Slide 1: State-based Equipment Qualification and DCS testability
China Techenergy Co., Ltd.
2013.09
Notes: women

## Slide 2
Content
1、Brief introduction of content
2、 Understanding of state-based equipment qualification source
3、Understanding of state-based equipment qualification theory/method
4、Examples of state-based equipment qualification and DCS testability
5、Technical points summary

## Slide 3: 1. Brief introduction of content
Brief introduction of content
  From the perspective of user expectations for instrumentation and control systems, the state-based equipment qualification is analyzed . To improve the state monitoring of equipment, the theories/methods of state-based equipment qualification are described, the key issue is the characteristic parameters of instrumentation and control systems.
  The relationship between characteristic parameters and diagnosis of existing standard is Analyzed , Examples of diagnosis design and state-based equipment qualification were provided, illustrating the compliance and non-compliance with existing standards; there also provides examples of state-based equipment qualification which beyond the scope of the existing standard.

## Slide 4: 2. Understanding of state-based equipment qualification source
State-based equipment qualification: All status of the instrumentation and control systems are to be monitored.
  key status of the instrumentation and control systems should be monitored ;
  More detailed information to key status should be provided;
  More status of the instrumentation and control systems should be monitored.

## Slide 5: 3. Understanding of state-based equipment qualification theories/methods
  Qualification program
    1.Monitoring characteristic parameters
    2.Ananlysis system health status
    3.Weak points location
    4.Alarm Indication
    5.Evaluation
  Notes Characteristic parameters represent the system health status
    Key status of the instrumentation and control systems should be monitored ;
    More detailed information to key status should be provided;
    More status of the instrumentation and control systems should be monitored.
3.1 Theories/methods of state-based equipment qualification
China Techenergy Co., Ltd.

## Slide 6: 3. Understanding of state-based equipment qualification principle
Definition of characteristic parameters
  Characteristic parameters represent the system health status which is the concerned by qualification and maintance.
Category of characteristic parameters
Category of characteristic parameters | Source of information
Environment status | Operation running monitor and control information
Processing equipment state | Operation running monitor and control information
Instrumentation and control equipment running status | Diagnostic message (Reflect experimental / testability)
Comprehensive health status | Based on expert system / neural network / fuzzy theory analysis obtained some status
3.2 Characteristic parameters
China Techenergy Co., Ltd.

## Slide 7: 3. Understanding of state-based equipment qualification principle
Monitored parameters
Characteristic parameters
Comprehensive health status
State-based equipment qualification
Already existed qualification
Expected equipment qualification
3.3 Characteristic parameters and equipment qualification
China Techenergy Co., Ltd.
Diagnostic information
Instrument and control equipments
Environment
Process equipments

## Slide 8: 4. Examples of state-based equipment qualification and DCS testability
    State-based equipment qualification and DCS testability: deal with diagnose ,experimental.
    Relationship of “diagnosis information and characteristic parameter”
      Diagnosis information belongs to characteristic parameter
      Characteristic parameter is not necessarily limited to diagnostic information required by exsiting standards
      Characteristic parameter is not necessarily dealed with as diagnostic information
    Examples in the list will be given:
 | Diagnosis | Status | Conform to state-based equipment qualification | Inconform to state-based equipment qualification
Existing standard | Completed diagnosis | Report status | √ | ×
 |  | Not report status | × | √
 | Uncompleted diagnosis | Not report status | × | √
The part beyond the existing standard | Characteristic parameter is not necessarily limited to diagnostic information required by exsiting standards |  | × | √
 | Characteristic parameter is not necessarily dealed with as diagnostic information |  | × | √
Example 1
Example 2
Example 3
Example 4
Example 5
4.1 Overview
China Techenergy Co., Ltd.

## Slide 9: 4. Examples of state-based equipment qualification and DCS testability
IEC60671 Nuclear power plants – Instrumentation and control systems important to safety –Surveillance testing
IEEE338 IEEE Standard Criteria for Periodic Surveillance Testing of Nuclear Power Generating Station Safety Systems
  Note: The existing standards require two aspects : self-diagnosis and periodic testing
4.2 Existing Standard
China Techenergy Co., Ltd.

## Slide 10: 4. Examples of state-based equipment qualification and DCS testability
Requirement of Self-diagnosis
Self-diagnosis requirement of IEC60671 standard | Characteristic parameters to be checked (status)
The integrity of stored program | The integrity of the Memory The integrity of the program
The ability to retain values of RAM | RAM in sound status (in sound: in good healthy )
The ability of processor correctly execute subset of instruction, such floating-point arithmetic | Processor CPU in sound status
Integrity of address and data busses | Address and data bus in sound status
The correctness of messages sent between the processors | Processors sending mechanism in sound status
Freshness of messages between asynchronous processors | Heartbeat status of asynchronous processor sending information
Correctness of memory access (data not accessed as program, non-overflow of stack, etc.) | Memory in sound status
Validity of process signal (range check, rate of change, etc.) | Valid status of signal processing
The correctness of the control flow of the program execution | Program execution in good status
Requirement of period test
  Residual failure without detected by self-diagnosis requires periodic test
4.2.1 Requirement of IEC60671
China Techenergy Co., Ltd.
Note: characteristic parameters should be based on assumed effect modes

## Slide 11: 4. Examples of state-based equipment qualification and DCS testability
requirements of Period test defined in IEEE338
  the ability to perform safety functions under normal environmental conditions be proved by period test
  the ability to perform safety functions under abnormal environmental conditions not be proved by period test but equipment qualification.
requirement of Period test in IEEE338 | Characteristic parameters to be checked (status)
Channel check | Status of channel
Functional test | Status of equipment
Verification of channel calibration | accurate of channel
Verification of response time | Status of response time
Logical system function test | Status of system
4.2.2 Requirement of IEEE338
China Techenergy Co., Ltd.

## Slide 12: 4. Examples of state-based equipment qualification and DCS testability
diagnostic information belongs to characteristic parameters , which abnormal status must be processed
Characteristic：
  Meet with the requirement of existing standard
  And can be realized by current technology level
  And status information can be reported
Example 1.1: Program execution state in intelligent boards
Example 1.2: Specially engineered safety features drive is in good or bad state
2013-9-13
12
维护状态区相应数据
4.3 例子 1——既有标准符合基于状态的设备鉴定
4.3 Example 1—The existing standard is conform to state-based equipment qualification

## Slide 13: 4. Examples of state-based equipment qualification and DCS testability
diagnostic information belongs to characteristic parameters, diagnostic information is not reported
Characteristic ：
  Meet with the requirement of existing standard
  And can be realized by current technology level
  Status information is not reported
Example 2: Flow control in network(RPR)
2013-9-13
13
维护状态区相应数据
4.3 Example 2-- The existing standard is not conform to state-based equipment qualification

## Slide 14: 4. Examples of state-based equipment qualification and DCS testability
diagnostic information belongs to characteristic parameters, but some diagnosis is not complete, the corresponding diagnostic information is not reported
Characteristic：
  Meet with the requirement of existing standard
  And can be realized by current technology level
  Diagnosis is not comprehensive which lead to cannot report all status information
Example 3: RAM diagnosis in the intelligent board
2013-9-13
14
维护状态区相应数据
4.3 Example 3 - existing standard does not meet with state-based equipment qualification
×
    Without diagnosis of stack area, abnormal state cannot be reported

## Slide 15: 4. Examples of state-based equipment qualification and DCS testability
Characteristic parameter is not necessarily limited to self-diagnostic required by standards
Characteristic：
  Existing standard have no requirements
  Or cannot be realized by current technology level
  Or status information is not reported
Example 4: temperature condition of processor chip in smart board
2013-9-13
15
维护状态区相应数据
4.3 Example 4 - beyond existing standards does not meet with state-based equipment qualification
×
×
×

## Slide 16: 4. Examples of state-based equipment qualification and DCS testability
Characteristic parameter is not necessarily processed as real-time monitoring information
Characteristic ：
  Existing standard have no requirements
  Or cannot be realized by current technology level
  Or status information cannot be reported
Example 5: number of malfunction in DO board
2013-9-13
16
维护状态区相应数据
4.3 Example 5 - beyond existing standards do not meet with state-based equipment qualification
×
×
×

## Slide 17: 5. Technical view summary
1. It’s necessary to carry out state-based equipment qualification and research of DCS testability;
2. It’s difficulty to carry out state-based equipment qualification and research of DCS testability, especially acquiring , analysis ,reporting information of characteristic parameters;
3. The qualification standards should be upgraded according to the levels of technical development and User expection.
Thanks!
China Techenergy Co., Ltd.