## Slide 1: IEEE P650 Status
Chair
Dennis Dellinger Ametek Solidstate Controls
Vice Chair
Kenneth Caldwell Duke Energy

## Slide 2: Purpose of Standard IEEE 650
To qualify inverters, battery chargers and ancillary equipment to meet the requirements for 1-E equipment.
It is specific to mild environments outside of the containment.
Addresses potential electrical, mechanical and environmental extremes.
To prove that the battery chargers and inverters perform their safety function under specified service conditions.

## Slide 3: Major changes to existing std.
The updates are not considered a change in direction, they are to be considered adjustments, to align to industry needs and parent standard updates.

## Slide 4: Change to Document Title
Standard for Qualification of Class 1E Static
Battery Chargers, Inverters and Uninterruptible Power
Supply (UPS) Systems for Nuclear Power Generating Stations

## Slide 5: Change to Scope Statement
This standard describes methods for qualifying, static battery chargers, inverters and uninterruptible power supply (UPS) systems for Class 1E installations outside containment in nuclear power generating stations.

## Slide 6: References
All references to be updated to latest revisions.
Several new references will be added.

## Slide 7: Add Section 3.10
3.10 Uninterruptible Power Supply (UPS): a system designed to provide power automatically, without delay or transients during any period when the normal power supply is incapable of performing acceptably [IEEE 100]. The UPS may consist of and not limited to the following modules/sections:

## Slide 8: Add Section 3.10 (continued)
Inverter
Battery charger
Rectifier
Static transfer switch
Maintenance bypass switch
Battery power source
Line regulating transformer

## Slide 9: Environment (4.3)
Need to consider additional EMI/RFI relaxation limits for voltages above those addressed in MIL 461 and high power equipment.

## Slide 10: Figure 1
Will be updated to cover new items and changes within the body of the standard

## Slide 11: ADD Section 5.1.?
Add section requiring Software Analysis
“Software Verification and Validation shall be performed as defined in NRC Reg. Guide 1.152-2011.”

## Slide 12: ADD Section 5.3.1.?
Transient Test
The equipment shall be subject to a transient test on the AC input lines. The test shall incorporate a transient to verify that the critical loads are not affected by a disturbance on the input AC lines
If the equipment design is such that a suspend operations is encountered, the equipment must restart and resume normal operation without intervention

## Slide 13: Transient test Cont.
The transient shall be in accordance with figure X and the levels presented are to be considered minimum levels for the test
For high kva rated equipment where a variable input source is not attainable, the test may be performed on a identical design system of lower kva rating to verify functional compatibility

## Slide 14: Addition of Annex G
Considering adding an informative annex on power quality and reliability

## Slide 15: Plans for completion
Present to SC-2 at 14-2
Incorporate SC-2 Comments
Final Presentation and Review at SC-2 15-1 Meeting
Present to NPEC at 15-2
Submit for Ballot upon Approval from NPEC