## Slide 1: UC BERKELEY MEDIUM VOLTAGE GROUNDING SYSTEM
PRESENTATION TO IEEE EDUCATION AND HEALTHCARE FACILITIES COMMITTEE
JERRY JIMENEZ, P.E.
SUPERVISOR, ELECTRICAL ENGINEERING
UTILITY ENGINEERING DEPARTMENT
UNIVERSITY OF CALIFORNIA, BERKELEY
SEPT. 20, 2016

## Slide 2: UC Berkeley Campus, with San Francisco in background.

## Slide 3: Oldest remaining of the original buildings – South Hall. Built 1886. Several other buildings built in 1870’s and 1880’s were destroyed by fire or earthquakes. First building (other than Mechanical Arts Building) to receive electric power (around 1894).

## Slide 4: Steam Plant, built in 1904. Provided steam and electricity to campus from 1904-1930. The exterior is noted for its WPA mosaic murals depicting street musicians and artisans.

## Slide 5: Steam Plant, built in 1930

## Slide 6: Steam Plant with Addition of Cogen, to the left. Cogen added in 1986.

## Slide 7: Lawrence Berkeley Lab (LBL) yellow perimeter; UC Berkeley red perimeter.

## Slide 8: LBL Cyclotron, built in 1931. First Cyclotron ever built. Current application is as the Advanced Light Source. LBL was founded by Ernest Orlando Lawrence in 1931. LBL is the oldest of the National Laboratories. LBL is funded by DOE and managed by the University of California. It is a completely separate entity from UC Berkeley.

## Slide 9: 16 Chemical Elements have been discovered at Lawrence Berkeley Lab

## Slide 10: UCB/LBL Single Line 1963-1986

## Slide 11: UCB/LBL Single Line 1986-1999

## Slide 12: UCB/LBL Single Line Diagram 1999- Present

## Slide 13: 7.2 Ohm Grounding Resistor shown to left of transformer. Resistor is connected from transformer X0 bushing to ground.

## Slide 14: Grounding resistor has a 10 second rating. Note ventilation louvers. I2 R = 7.2 MW!

## Slide 15: Grounding resistor nameplate. Provides 1000 amps of current for a solid ground fault.

## Slide 16: Zig-Zag grounding transformer for Cogen Plant. 119.4 ohms Zero Sequence. Also connected is a 36 ohm, 7.2 kV rated resistor from H0 to ground. Provides 180 amps of current for a solid ground fault.

## Slide 17: Advantages of a Low Resistance Grounding System
Limits ground fault current and damage
CT’s do not saturate during ground faults. Prior to converting to low resistance grounding from solid grounding, we had several instances of CT’s saturating due to high level faults. This resulted in upstream breakers tripping, which caused a larger outage than should have occurred. Note that we have high available fault current of approximately 26,000 amps, partially due to the contribution of the Cogen Plant.

## Slide 18: Disadvantages of Low Resistance Grounding
When a ground fault occurs, the voltage to ground on the unfaulted phases increases to 12.47 kV. With a solidly grounded system, the voltage to ground on the unfaulted phases remains close to 7.2 kV. For this reason, we utilize 133% insulation on our 15 kV cable.
Most of our 12 kV switchgear PT’s are connected wye-wye, with the primary side connected phase-to-ground. As a result, during a ground fault on the 12 kV system, the voltage across the primaries of the PT’s for the unfaulted phases increases from the normal value of 7.2 kV to as high as 12.47 kV. We have had several occasions where PT fuses blew following a ground fault on the 12 kV system.
Distribution Transformers should have delta winding for 12 kV primary (not wye).
Surge arresters must be rated 12 kV with a 10.2 kV MCOV. With a solidly grounded system, they would be of a lower rating.